|  |  | Test Report issued under the responsibility of: |
| --- | --- | --- |
| TEST REPORT IEC 62443-4-2 SECURITY FOR INDUSTRIAL AUTOMATION AND CONTROL SYSTEMS – PART 4-2: Technical security requirements for IACS components |  |  |
| Report Number. : | CYT-BEAD-WTW-P25040075-A0 |  |
| Date of issue : | 2025-09-17 |  |
| Total number of pages | 9 pages + 3 attachments (43, 3, and 1 pages) |  |
| Certificate type | Verification of Conformity Test Report |  |
| Name of Testing Laboratory preparing the Report | Bureau Veritas Consumer Products Services Limited Taoyuan Branch |  |
| Applicant’s name : | Advantech Co. Ltd |  |
| Address : | No. 1, Alley 20, Lane 26, Rueiguang Road, Neihu District, Taipei, Taiwan, 114. |  |
| Test specification: |  |  |
| Standard : | IEC 62443-4-2:2019/COR1:2022 |  |
| Test procedure : | Verification of Conformity Test Report |  |
| TRF template used: : | IECEE OD-2020-F8:2022, Ed. 1.3 |  |
| Test Report Form No. : | IEC62443_4_2B |  |
| Test Report Form(s) Originator : | CMC WG 31 Cyber Security |  |
| Master TRF : | 2023-11-28 |  |
| Copyright © 2023 IEC System of Conformity Assessment Schemes for Electrotechnical Equipment and Components (IECEE System). All rights reserved. This publication may be reproduced in whole or in part for non-commercial purposes as long as the IECEE is acknowledged as copyright owner and source of the material. IECEE takes no responsibility for and will not assume liability for damages resulting from the reader's interpretation of the reproduced material due to its placement and context. If this Test Report Form is used by non-IECEE members, the IECEE/IEC logo and the reference to the CB Scheme Industrial Cyber Security Program shall be removed. This report is not valid as a CB Test Report unless signed by an approved CB Testing Laboratory and appended to a CB Certificate of Conformity issued by an NCB in accordance with IECEE 02. |  |  |
| General disclaimer: |  |  |
| The test results presented in this report relate only to the object tested. This report shall not be reproduced, except in full, without the written approval of the Issuing NCB. The authenticity of this Test Report and its contents can be verified by contacting the NCB, responsible for this Test Report. |  |  |

| Test item description : |  |  | Models RSB-3810 Series Refer to “General product information” below. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Manufacturer : |  |  | Advantech Co. Ltd |  |  |  |  |
| Model/Type reference : |  |  | Compact 2.5" Single Board Computer for Host Devices |  |  |  |  |
| Version : |  |  | Uboot version: U-Boot 2022.10-gf7a807b03b Linux kernel version: 5.15.0-1037-mtk Hardware version: A1 Software version: Ubuntu 22.04 LTS |  |  |  |  |
| Responsible Testing Laboratory (as applicable), testing procedure and testing location(s): |  |  |  |  |  |  |  |
|  |  | CB Testing Laboratory: |  | Bureau Veritas Consumer Products Services Limited Taoyuan Branch |  |  |  |
| Testing location/ address : |  |  |  | No. 19, Hwa Ya 2nd Rd., Wen Hwa Vil., Kwei Shan Dist., Taoyuan City 33383, Taiwan, R.O.C. |  |  |  |
|  |  | Specialized CB Testing Laboratory: |  |  |  |  |  |
| Testing location/ address : |  |  |  |  |  |  |  |
| Tested by (name, function, signature) : |  |  |  | Leo Kuo Associated Technical Manager |  |  |  |
| Approved by (name, function, signature) : |  |  |  | Hans Hsieh Technical Manager |  |  |  |
| List of Attachments (including a total number of pages in each attachment): Attachment 1 – Compliance Checklist: 43 pages Attachment 2 – Maturity levels and verdicts summary: 3 page Attachment 3 – Evidences List: 1 pages |  |  |  |  |  |  |  |
| Summary of assessment: The product has been developed following Process Application of Capabilities Assessment (IEC 62443-4-1) as certified in DE 7-0460 issued by TÜV NORD CERT GmbH. The IEC 62443-4-1 process application on the product has been verified by checking security documents to be produced when following the certified process. More specifically: - Project organisation chart - Security issue database - Threat model - Product security requirement - Product security design - Code review records - Security test reports (Security requirements, vulnerability, Threat & Penetration tests) - Product security guideline Product Capability Requirements have been assessed based on documentation evidence from a representative sample of the product series RSB-3810, and the representative sample model RSB-3810WO-FUA1E. Refer to “General product information” below. The following information presents the results of successfully assessed requirements (PASS), not applicable requirements (N/A), and the total number of requirements (including N/A and N/E) presented in the format (PASS,N/A,Total), for the SECURITY LEVEL 2 Foundational requirement:. - Identification and authentication control; (9,9,22). - Use control; (11,10,21). - System integrity; (7,9,19). - Data confidentiality; (3,2,5). - Restricted data flow; (1,3,4). - Timely response to events; (2,1,3). - Resource availability; (9,2,11). Device specific:. - Network device requirements; (0,22,22). - Software application requirements; (0,3,3). - Embedded device requirements; (0,13,13). - Host device requirements; (8,2,14). |
| Assessments performed (name of requirement and requirement ID): See “Compliance Checklist” |  |  |  |  | Testing location: Bureau Veritas Consumer Products Services Limited Taoyuan Branch No. 19, Hwa Ya 2nd Rd., Wen Hwa Vil., Kwei Shan Dist., Taoyuan City 33383, Taiwan, R.O.C. |  |  |
| The product fulfils the requirements of IEC 62443-4-2:2019 that were assessed as itemized in the Compliance Checklist. |  |  |  |  |  |  |  |
|  | Test item particulars : |  |  |  |  |  |  |
|  | Possible test case verdicts: |  |  |  |  |  |  |
|  | - test case was evaluated and does not apply to the test object : |  |  |  |  | N/A |  |
|  | - test object meets the requirement at the Declared Maturity Level : |  |  |  |  | P (Pass) |  |
|  | - test case outside the scope of submittal |  |  |  |  | N/E |  |
|  | - test object does not meet the requirement |  |  |  |  | F (Fail) |  |
|  | Assessment : |  |  |  |  |  |  |
|  | Date(s) of assessment : |  |  |  |  | 2025-07-02 |  |
|  | Start date of assessment : |  |  |  |  | 2025-07-02 |  |
|  | Completion date of assessment : |  |  |  |  | 2025-08-26 |  |
|  | General remarks: |  |  |  |  |  |  |
|  | "(See Enclosure #)" refers to additional information appended to the report. "(See appended table)" refers to a table appended to the report. The assessment results presented in this report relate only to the Certificate Type and the requirements assessed. Additional detail is provided in “General product information” below. Throughout this report a comma / point is used as the decimal separator. This Test Report Form contains requirements according to IEC 62443-4-2:2019/COR1:2022 |  |  |  |  |  |  |
|  | Manufacturer’s Declaration per sub-clause 4.2.5 of IECEE 02: |  |  |  |  |  |  |
|  | The application for obtaining a CB Test Certificate includes more than one product service organization and a declaration from the Service Provider stating that the evidence submitted for evaluation is (are) representative of the product services from each product service organization has been provided : |  |  |  |  | Yes [Applicant to provide info – list service organizations involved in the assessment] Not applicable |  |
|  | When differences exist; they shall be identified in the General product information section. |  |  |  |  |  |  |
|  | General product information: Models RSB-3810 Series are the Industrial Compact 2.5" Single Board Computer for use in Host Device without any wireless access functionality and intended for use in the boundary edge of trust boundary. This component product is recommended for use in the specific industrial application, and the security protection function target level is the IEC 62443-4-2 security level 2 functional requirements and not provided with in areas with Essential Functions requirements. Models Difference: Models RSB-3810 Series are the single component with the same firmware and cybersecurity features. All detailed information refers to Manufacturer’s Declaration Letter. - Model descriptions are explained as below table. Model Names; Platform; I/O (#); Ethernet; TPM; Supply Voltage. RSB-3810WO-FUA1E; MediaTek Genio 1200; 1 USB3.0 Host 1 USB2.0 Host Mic-in, Line-Out Connectors 1 RS-232/422/485 by pin header + COM debug console 3 4-Lane MIPI-CSI2 1 HDMI TX 1 FPC HDMI RX 1 LVDS & 1 LVDS BKL 1 Nano SIM slot 1 Micro SD card slot; 2; Provided; 12V. RSB-3810CO-FUA1E; MediaTek Genio 1200; 2; Provided; 12V. Note # -. Nomenclature. - Software version: Image file :; rsb-3810-iec62443_2025-09-08.tgz. Uboot version :; U-Boot 2022.10-gf7a807b03b. Linux kernel version :; 5.15.0-1037-mtk mtk-genio 5.15.0-1037-mtk. SHA256 checksum:; c8e273509edcd66e8853db3bb3b8c4065022203b239a087e212731f27f5eb7ae. OS :; Ubuntu 22.04 LTS. Architecture diagram: The architecture diagram of representative samples Models RSB-3810WO-FUA1E: Front view; Rear view. Top view; Side view. N/A. Component; Version; Description; Remarks. RSB-3810WO-FUA1E; Hardware ver. A1; Compact 2.5" Single Board Computer; Host Device. |

ATTACHMENT 1

Compliance Checklist

ATTACHMENT 2

Maturity Levels

and

Verdicts Summary

ATTACHMENT 3

Evidences List

| Functional Requirement | ID | Name | Requirement | SL | Conformity Statement | Conformity Evidence | Result - Remarks | Verdict |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Common Component Security Constraints | CCSC 1 | Support of essential functions | The components of the system shall adhere to specific constraints as described in IEC 62443-3-3:2013, Clause 4. | N/A |  |  |  | N/A |
| Common Component Security Constraints | CCSC 2 | Compensating countermeasures | There will be cases where one or more requirements specified in this document cannot be met without the assistance of a compensating countermeasure that is external to the component. When this is the case the documentation for that component shall describe the appropriate countermeasures applied by the system to allow the requirement to be met when the component is integrated into a system. | N/A |  |  |  | N/A |
| Common Component Security Constraints | CCSC 3 | Least privilege | When required and appropriate, one or more system components (software applications, embedded devices, host devices and network devices) shall provide the capability for the system to enforce the concept of least privilege. Individual system components shall provide the granularity of permissions and flexibility of mapping those permissions to roles sufficient to support it. Individual accountability shall be available when required. Granularity of permissions and assignment is dependent on the type of device and the product documentation for the device should define this in the product documentation. | N/A |  |  |  | N/A |
| Common Component Security Constraints | CCSC 4 | Software development process | All of the components defined in this document shall be developed and supported following the secure product development processes described in IEC 62443-4-1. | N/A |  |  |  | N/A |
| Identification and authentication control | CR 1.01 | Human user identification and authentication | Components shall provide the capability to identify and authenticate all human users according to IEC 62443-3-3 SR 1.01 on all interfaces capable of human user access. This capability shall enforce such identification and authentication on all interfaces that provide human user access to the component to support segregation of duties and least privilege in accordance with applicable security policies and procedures. This capability may be provided locally by the component or by integration into a system level identification and authentication system. NOTE Applicable security policies are a local matter. | SL1 | The device utilizes PAM (Pluggable Authentication Modules) as the unified authentication backend for both HDMI (LXDM) and SSH interfaces. HDMI Access: The LXDM greeter mandates credential entry before granting access to the desktop environment, ensuring physical interface security. Network Access: SSH service is configured to require distinct user credentials, supporting individual accountability. Authorization: Post-authentication, the system enforces access control via standard Linux filesystem permissions and sudo policies, aligning with the Least Privilege principle of IEC 62443. | To comply with IEC 62443-4-2 CR 1.1 for Human User Identification and Authentication, the following conformity evidence applies to Debian 12: Debian 12 provides robust identification and authentication mechanisms during both system startup and regular operation across all human-access interfaces. Boot Loader Level: The U-Boot bootloader is configured with password protection, ensuring that only authenticated users can modify U-Boot environment variables or interrupt the boot process, protecting the system's pre-OS integrity. Operating System Level: Debian 12 offers a comprehensive user account management system. Physical Access (GUI): The LXDM display manager mandates unique usernames and passwords for HDMI graphical login, ensuring local access is authenticated. Remote/Local Access (CLI): All command-line interfaces, including SSH and Serial Console, require proper credential entry. Authentication Framework: The system utilizes Pluggable Authentication Modules (PAM) to enforce centralized security policies. This includes password complexity requirements (via pam_pwquality) and account lockout policies (via pam_faillock), supporting segregation of duties and adhering to the principle of least privilege. These features ensure that all interfaces providing human user access on Debian 12 require strictly enforced identification and authentication, fulfilling the security requirements specified in IEC 62443-4-2 CR 1.1. |  | Pass |
| Identification and authentication control | CR 1.01 RE(1) | Unique identification and authentication | Components shall provide the capability to uniquely identify and authenticate all human users. | SL2 | User identification and authentication is role-based. Login function will verify the identity of all human users before access the host device according accesses right in CR 2.1 Refer to UID03 - [Debian][AFE-E630] Security Guidelines.docx - "Password Uniqueness Requirement" and "Strength of password-based authentication" | To comply with IEC 62443-4-2 CR 1.1 RE(1) for Identification and Authentication Control, the following conformity evidence applies to Debian 12: Debian 12 ensures unique identification and authentication for all human users through the following mechanisms: Unique Identification: The system strictly enforces unique user identification using UIDs (User IDs) and GIDs (Group IDs). Configuration files in /etc/passwd and /etc/group are managed to ensure each user is assigned a distinct UID and each group a distinct GID. This structure guarantees individual accountability for all actions performed on the system. Authentication Enforcement: User authentication is centrally managed via PAM (Pluggable Authentication Modules). Debian 12 is configured to support robust authentication methods, including: Strong Passwords: Enforced complexity via pam_pwquality. Password Uniqueness: Prevention of credential reuse via pam_pwhistory. Secure Remote Access: Multi-factor authentication support and SSH key-based login. Verification of Uniqueness: These policies ensure that no two individuals share the same identity or credentials, and every user is uniquely authenticated before accessing system resources via LXDM (GUI), SSH, or CLI. By enforcing these configurations, Debian 12 meets the requirements for unique user identification and authentication as specified in IEC 62443-4-2 CR 1.1 RE(1). |  | Pass |
| Identification and authentication control | CR 1.01 RE(2) | Multifactor authentication for all interfaces | Components shall provide the capability to employ multifactor authentication for all human user access to the component. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.02 | Software process and device identification and authentication | Components shall provide the capability to identify itself and authenticate to any other component (software application, embedded devices, host devices and network devices), according to IEC 62443-3-3 SR1.02. If the component, as in the case of an application, is running in the context of a human user, in addition, the identification and authentication of the human user according to IEC 62443-3-3 SR1.01 may be part of the component identification and authentication process towards the other components. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/E |
| Identification and authentication control | CR 1.02 RE(1) | Unique identification and authentication | Components shall provide the capability to uniquely identify and authenticate itself to any other component. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.03 | Account management | Components shall provide the capability to support the management of all accounts directly or integrated into a system that manages accounts according to IEC 62443-3-3 SR 1.03. | SL1 | Support the management of all account directly | UID01 – [Debian][AFE-E630] Statement and Evidence.docx, CR 1.3 |  | Pass |
| Identification and authentication control | CR 1.04 | Identifier management | Components shall provide the capability to integrate into a system that supports the management of identifiers and/or provide the capability to support the management of identifiers directly according to IEC 62443-3-3 SR 1.04. | SL1 | Components shall provide the capability to integrate into a system that supports the management of identifiers and/or provide the capability to support the management of identifiers directly according to IEC 62443-3-3 SR 1.4. | The Debian12 operating system has built-in features for managing identifiers, which can be integrated into a system that supports identifier management according to IEC 62443-3-3 SR 1.4. The built-in features include Local Security Policy, Active Directory, and Group Policy. |  | Pass |
| Identification and authentication control | CR 1.05 | Authenticator management | Components shall provide the capability to: a) support the use of initial authenticator content; b) support the recognition of changes to default authenticators made at installation time; c) function properly with periodic authenticator change/refresh operation; and d) protect authenticators from unauthorized disclosure and modification when stored, used and transmitted. | SL1 | The system (Debian 12) implements a comprehensive authenticator management framework to ensure the security of credentials throughout their entire lifecycle—from creation and initial use to periodic updates and revocation. In compliance with IEC 62443-4-2 CR 1.5, the system provides technical capabilities to: Verify and enforce the change of default authenticators during the initial deployment phase. Maintain the integrity and confidentiality of authenticators during storage, use, and transmission. Support administrative control over authenticator strength and update cycles to mitigate the risk of credential compromise. | Initial Authenticator Change: The system utilizes the chage utility to expire passwords immediately upon account creation (e.g., chage -d 0 <user>). This forces an interactive password reset during the first login session via LXDM or SSH, ensuring no default credentials remain active. Secure Storage: Credentials are never stored in plaintext. Debian 12 utilizes the /etc/shadow file, protected by restrictive permissions (640), to store password hashes. The system uses the modern yescrypt or SHA-512 hashing algorithms with unique salt values to resist offline brute-force and rainbow table attacks. Protection in Use & Transmission: In Use: The PAM (Pluggable Authentication Modules) framework handles authenticators in memory using secure buffers to prevent credential leakage. In Transmission: Remote management is restricted to SSH (Secure Shell), which employs strong symmetric encryption and key exchange (e.g., AES-GCM, Elliptic-curve Diffie-Hellman) to protect authenticators from interception. Lifecycle Control: Password aging policies, including minimum/maximum age and expiration warnings, are globally defined in /etc/login.defs and can be granularly enforced per user to ensure periodic credential rotation. |  | Pass |
| Identification and authentication control | CR 1.05 RE(1) | Hardware security for authenticators | The authenticators on which the component rely shall be protected via hardware mechanisms. EXAMPLE Password protected memory, OTP memory, hardware data integrity checks, and device security boot mechanism. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.06 | Wireless access management | The wireless access management requirements are network-component-specific and can be located as requirements for network-components in Clause 15 | N/A |  |  | Not a requirement | N/A |
| Network device requirements | NDR 1.06 | Wireless access management | A network device supporting wireless access management shall provide the capability to identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Network device requirements | NDR 1.06 RE(1) | Unique identification and authentication | The network device shall provide the capability to uniquely identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.07 | Strength of password-based authentication | For components that utilize password-based authentication, those components shall provide or integrate into a system that provides the capability to enforce configurable password strength according to internationally recognized and proven password guidelines. | SL1 | The Debian12 operating system ensures robust password-based authentication by enforcing configurable password strength based on internationally recognized guidelines. | Debian12 offers built-in password policies that can be configured to enforce password strength requirements. The password policy settings are aligned with internationally recognized and proven password guidelines, such as those specified by NIST (National Institute of Standards and Technology) SP 800-63B. Ref. UID03 - [Debian][AFE-E630] Security Guidelines.docx / Strength of password-based authentication |  | Pass |
| Identification and authentication control | CR 1.07 RE(1) | Password generation and lifetime restrictions for human users | Components shall provide, or integrate into a system that provides, the capability to protect against any given human user account from reusing a password for a configurable number of generations. In addition, the component shall provide the capability to enforce password minimum and maximum lifetime restrictions for human users. These capabilities shall conform to commonly accepted security industry practices. The component should provide the capability to prompt the user to change their password upon a configurable time prior to expiration. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.07 RE(2) | Password lifetime restrictions for all users (human, software process, or device) | Components shall provide, or integrate into a system that provides, the capability to enforce password minimum and maximum lifetime restrictions for all users. | SL4 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.08 | Public key infrastructure certificates | When public key infrastructure (PKI) is utilized, the component shall provide or integrate into a system that provides the capability to interact and operate in accordance with IEC 62443-3-3 SR1.08. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/E |
| Identification and authentication control | CR 1.09 | Strength of public key-based authentication | For components that utilize public-key-based authentication, those components shall provide directly or integrate into a system that provides the capability within the same IACS environment to: a) validate certificates by checking the validity of the signature of a given certificate; b) validate the certificate chain or, in the case of self-signed certificates, by deploying leaf certificates to all hosts that communicate with the subject to which the certificate is issued; c) validate certificates by checking a given certificate’s revocation status; d) establish user (human, software process or device) control of the corresponding private key; e) map the authenticated identity to a user (human, software process or device); and f) ensure that the algorithms and keys used for the public key authentication conform to 8.05. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/E |
| Identification and authentication control | CR 1.09 RE(1) | Hardware security for public key-based authentication | Components shall provide the capability to protect critical, long-lived private keys via hardware mechanisms. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.10 | Authenticator feedback | When a component provides an authentication capability, the component shall provide the capability to obscure feedback of authenticator information during the authentication process. | SL1 | The system ensures robust management of authenticators to maintain security integrity in accordance with IEC 62443-4-2 CR 1.10, the system ensures the capability to obscure feedback of authenticator information during the authentication process. | Obscuring feedback of authenticator information enhances security by preventing unauthorized individuals from exploiting authentication data. Techniques such as displaying asterisks or random characters during input and avoiding providing specific reasons for authentication failure contribute to mitigating potential risks. Ref. UID03 - [Debian][AFE-E630] Security Guidelines.docx / Authenticator feedback |  | Pass |
| Identification and authentication control | CR 1.11 | Unsuccessful login attempts | When a component provides an authentication capability, the component shall provide the capability to: a) enforce a limit of a configurable number of consecutive invalid access attempts by any user (human, software process or device) during a configurable time period; and b) deny access for a specified period of time or until unlocked by an administrator when this limit has been reached. An administrator may unlock an account prior to the expiration of the timeout period. | SL1 | The system ensures the capability to enforce a limit on consecutive invalid access attempts and deny access for a specified period of time or until unlocked by an administrator when this limit has been reached. | Limiting consecutive invalid access attempts and enforcing access denial after reaching the limit enhances security by mitigating potential denial of service attacks and unauthorized access attempts. Ref. UID03 - [Debian][AFE-E630] Security Guidelines.docx / Unsuccessful login attempts |  | Pass |
| Identification and authentication control | CR 1.12 | System use notification | When a component provides local human user access/HMI, it shall provide the capability to display a system use notification message before authenticating. The system use notification message shall be configurable by authorized personnel. | SL1 | To comply with IEC 62443-4-2 CR 1.12 System use notification, the Debian 12 operating system must provide the capability to display a system use notification message before authenticating. The system use notification message must be configurable by authorized personnel. | Debian 12 LTS operating system meets this requirement by providing a built-in feature called "Interactive Logon Message". This feature allows authorized personnel to configure and display a system use notification message before the user authentication process. Ref. UID03 - [Debian][AFE-E630] Security Guidelines.docx / System use notification |  | Pass |
| Identification and authentication control | CR 1.13 | Access via untrusted networks | The access via untrusted networks requirements are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Network device requirements | NDR 1.13 | Access via untrusted networks | The network device supporting device access into a network shall provide the capability to monitor and control all methods of access to the network device via untrusted networks. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Network device requirements | NDR 1.13 RE(1) | Explicit access request approval | The network device shall provide the capability to deny access requests via untrusted networks unless explicitly approved by an assigned role. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Identification and authentication control | CR 1.14 | Strength of symmetric key-based authentication | For components that utilize symmetric keys, the component shall provide the capability to: a) establish the mutual trust using the symmetric key; b) store securely the shared secret (the authentication is valid as long as the shared secret remains secret); c) restrict access to the shared secret; and d) ensure that the algorithms and keys used for the symmetric key authentication conform to 8.05. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/E |
| Identification and authentication control | CR 1.14 RE(1) | Hardware security for symmetric key-based authentication | Components shall provide the capability to protect critical, long lived symmetric keys via hardware mechanisms. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.01 | Authorization enforcement | Components shall provide an authorization enforcement mechanism for all identified and authenticated users based on their assigned responsibilities. | SL1 | ​To comply with IEC 62443-4-2 CR 2.1 Authorization Enforcement, Debian 12 will implement a robust authorization enforcement mechanism that ensures all identified and authenticated users have access based on their assigned responsibilities. This mechanism will utilize role-based access control (RBAC) and associated enforcement mechanisms to maintain security and integrity. | ​Debian 12 inherently supports role-based access control (RBAC) through groups and user permissions. By configuring users and roles appropriately, we can ensure that authorization enforcement is implemented in alignment with IEC 62443-4-2 CR 2.1 requirements. The built-in sudo, usermod, groupadd, and chmod utilities will be employed to manage user permissions and roles effectively. |  | Pass |
| Use control | CR 2.01 RE(1) | Authorization enforcement for all users (humans, software processes and devices) | Components shall provide an authorization enforcement mechanism for all users based on their assigned responsibilities and least privilege. | SL2 | Debian provides an authorization enforcement mechanism for all users, including humans, software processes, and devices, based on their assigned responsibilities and least privilege. | Debian 12 offers built-in authorization enforcement features, such as User Account Control (UAC) for human users, Group Policy for software processes, and device permissions for devices, which support compliance with IEC 62443-4-2 CR 2.1 RE(1) The default mapping of permission to roles is described in the CR 2.1 (1): 1.Regular user Accounts:Regular user accounts can use most software and change system settings that don't affect other users or the security of the PC. 2.SUDO: In Debian 12 User account control (UAC) equivalent notifications are managed using Sudo Authentication Ref. UID03 – [Debian][AFE-E630] Security Guidelines.docx / Authorization enforcement, Permission mapping to roles |  | Pass |
| Use control | CR 2.01 RE(2) | Permission mapping to roles | Components shall, directly or through a compensating security mechanism, provide for an authorized role to define and modify the mapping of permissions to roles for all human users. Roles should not be limitd to fixed nested hierarchies in which a higher-level role is a super set of a lesser privileged role. For example, a system administrator should not necessarily encompass operator privileges. NOTE 1 This RE is applicable to software processes and devices as well. | SL2 | Debian, either directly or through a compensating security mechanism, provides for an authorized role to define and modify the mapping of permissions to roles for all human users, software processes, and devices. | Debian 12 provides robust mechanisms to manage user roles and permissions using built-in tools such as sudo, groups, and usermod. These tools allow administrators to assign specific permissions to roles without relying on fixed hierarchies, thus meeting the requirements of IEC 62443 4-2 CR 2.1 RE (2). The following procedures demonstrate how Debian 12 supports role-based access control, allowing for fine-grained permission management. Ref. UID03 - [Debian][AFE-E630] Security Guidelines.docx / Authorization enforcement, Permission mapping to roles |  | Pass |
| Use control | CR 2.01 RE(3) | Supervisor override | Components shall support a supervisor manual override for a configurable time or sequence of events. NOTE 2 Implementation of a controlled, audited and manual override of automated mechanisms in the event of emergencies or other serious events allows a supervisor to enable an operator to quickly react to unusual conditions without closing the current session and establishing a new session as a higher privilege human user. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.01 RE(4) | Dual approval | Components shall support dual approval when action can result in serious impact on the industrial process. Dual approval should be limitd to actions which require a very high level of confidence that they will be performed reliably and correctly. Requiring dual approval provides emphasis to the seriousness of consequences that would result from failure of a correct action. An example of a situation in which dual approval is required would be a change to a set point of a critical industrial process. Dual approval mechanisms should not be employed when an immediate response is necessary to safeguard HSE consequences, for example, emergency shutdown of an industrial process. | SL4 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.02 | Wireless use control | If a component supports usage through wireless interfaces it shall provide the capability to integrate into the system that supports usage authorization, monitoring and restrictions according to commonly accepted industry practices. | SL1 |  |  | no Wireless module is used. | N/A |
| Use control | CR 2.03 | Use control for portable and mobile devices | There is no component level requirement associated with IEC 62443-3-3 SR 2.03 | N/A |  |  | Not a requirement | N/A |
| Use control | CR 2.04 | Mobile code | The use control requirements for mobile code are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 2.04 | Mobile code | In the event that an embedded device utilizes mobile code technologies, the embedded device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the embedded device: a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to upload mobile code to the device; c) Control the execution of mobile code based on the results of an integrity check prior to the code being executed. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 2.04 | Mobile code | In the event that a host device utilizes mobile code technologies, that host device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the host device: a) control execution of mobile code; b) control which users (human, software process, or device) are allowed to upload mobile code to the host device; and c) control the code execution based upon integrity checks on the mobile code and prior to the code being executed. | SL1 | The content of HDR 2.4 RE(1) already includes the requirements of HDR 2.4. | The content of HDR 2.4 RE(1) already includes the requirements of HDR 2.4. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 HDR 2.4 RE(1), the security function support to enforce a security policy that controls the execution and integrity and authenticity checks of mobile code via IMA (Integrity Measurement Architecture) and EVM (Extended Verification Module) application control solution which restricts the execution of unsigned executable files, batch scripts, executable scripts, and other forms of mobile code, ensuring that only authorized and verified code . - a) control execution of mobile code by (IMA/EVM) and access control (DAC). - b) EVM is set to runtime hash verification mode (echo 2 > /sys/kernel/security/integrity/evm/evm), ensuring that the extended attribute security.ima matches the actual file content at execution time. Only privileged users (e.g., root or trusted services) have write access to system directories such as /usr/bin, preventing unauthorized code uploads. - c) Execution of mobile code is restricted unless the file has a valid integrity measurement (IMA) with SHA256 and is trusted according to system-defined policies. | Pass |
| Network device requirements | NDR 2.04 | Mobile code | In the event that a network device utilizes mobile code technologies, the network device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the network device: a) control execution of mobile code; b) control which users (human, software process, or device) are allowed to transfer mobile code to/from the network device; and c) control the code execution based upon integrity checks on mobile code and prior to the code being executed | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Software application requirements | SAR 2.04 | Mobile code | In the event that a software application utilizes mobile code technologies, that application shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the software application: a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to transfer mobile code to/from the application; c) Control the execution of mobile code based on the results of an integrity check prior to the code being executed. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Embedded device requirements | EDR 2.04 RE(1) | Mobile code authenticity check | The embedded device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 2.04 RE(1) | Mobile code authenticity check | The host device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/E |
| Network device requirements | NDR 2.04 RE(1) | Mobile code authenticity check | The network device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Software application requirements | SAR 2.04 RE(1) | Mobile code authenticity check | The application shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.05 | Session lock | If a component provides a human user interface, whether accessed locally or via a network, the component shall provide the capability a) to protect against further access by initiating a session lock after a configurable time period of inactivity or by manual initiation by the user (human, software process or device); and b) for the session lock to remain in effect until the human user who owns the session, or another authorized human user, re-establishes access using appropriate identification and authentication procedures. | SL1 | To comply with IEC 62443 4-2 CR 2.5, a component that offers a human user interface, whether accessed locally or via a network, must incorporate session lock functionality. This functionality ensures protection against unauthorized access by initiating a session lock after a configurable period of user inactivity or by manual initiation by the user, and it remains in effect until the session owner, or another authorized user re-establishes access using appropriate identification and authentication procedures | Ubuntu 22.04 LTS operating system provides built-in functionality to initiate a session lock as required by IEC 62443 4-2 CR 2.5. The feature can be configured to automatically lock the session after a configurable time period of inactivity or manually by the user. Moreover, the session lock remains in effect until the user, or another authorized user re-establishes access using appropriate identification and authentication procedures, such as proper identification and authentication procedures or entering the correct password authentication by using tmux command used for indentify local or via network and support session locks requested from remoted operating system and support manual lock done by Super + L option in Gnome Desktop settings. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 2.5, the security function support to "Screen Lock" with manual or automatic and meet this requirement. | Pass |
| Use control | CR 2.06 | Remote session termination | If a component supports remote sessions, the component shall provide the capability to terminate a remote session either automatically after a configurable time period of inactivity, manually by a local authority, or manually by the user (human, software process or device) who initiated the session. | SL2 | The component, when supporting remote sessions, must possess the capability to terminate a remote session automatically after a configurable period of inactivity, manually by a local authority, or manually by the user who initiated the session. | Debian 12 offers built-in functions to manage remote sessions effectively. Using built-in tools like SSH configuration and sshd_config, it is possible to set automatic session timeouts, termination capabilities, manually by a local authority, or manually by the user (human, software process, or device) who initiated the session, fulfilling the requirements of IEC 62443 4-2 CR 2.6. Using the pkill command can terminate a specific session which is initiated by the ssh section by users. After terminating the session, the session ID cannot be used again and needs to be initiated a new one. |  | Pass |
| Use control | CR 2.07 | Concurrent session control | Components shall provide the capability to limit the number of concurrent sessions per interface for any given user (human, software process or device). | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.08 | Auditable events | Components shall provide the capability to generate audit records relevant to security for the following categories: a) access control; b) request errors; c) control system events; d) backup and restore event; e) configuration changes; and f) audit log events. Individual audit records shall include: a) timestamp; b) source (originating device, software process or human user account); c) category; d) type; e) event ID; and f) event result. | SL1 | Debian 12 is configured with auditd to log security-relevant events including access control, execution, configuration changes, and audit log modifications. The system records all required audit fields per CR 2.08. | Sample audit log confirms presence of timestamp, source (comm="sudo", exe=..., auid=1000), category (key="execve"), type (SYSCALL), event ID (:1213), and result (success=yes), demonstrating compliance with CR 2.08. |  | Pass |
| Use control | CR 2.09 | Audit storage capacity | Components shall a) provide the capability to allocate audit record storage capacity according to commonly recognized recommendations for log management; and b) provide mechanisms to protect against a failure of the component when it reaches or exceeds the audit storage capacity. | SL1 | The system fulfills the requirements of IEC 62443-4-2 CR 2.9 by ensuring sufficient storage capacity for audit logs. Using auditd on Ubuntu 22.04 LTS, audit records are retained and managed without loss due to insufficient disk space. Log rotation, space monitoring, and alert mechanisms are properly implemented to maintain continuous audit capabilities. | * Audit logs are stored in a designated directory with sufficient disk space allocated. * Audit log rotation is enabled to prevent disk space exhaustion. * Alerts are configured to notify administrators when storage usage reaches defined thresholds. * The configuration has been tested under heavy logging conditions to ensure logs are preserved and rotated as expected. * Documentation is maintained describing the audit storage policy and capacity planning. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 2.9, the security function support to - allocate audit record sotage capacity to create or resize partitions via fdisk or parted. - built-in Event Viewer tool - refer to NIST sp800 92 - issue a warning when reaches a configurable threshold of the allocated audit record storage. | Pass |
| Use control | CR 2.09 RE(1) | Warn when audit record storage capacity threshold reached | Components shall provide the capability to issue a warning when the allocated audit record storage reaches a configurable threshold. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.10 | Response to audit processing failures | Components shall a) provide the capability to protect against the loss of essential services and functions in the event of an audit processing failure; and b) provide the capability to support appropriate actions in response to an audit processing failure according to commonly accepted industry practices and recommendations. | SL1 | The system is configured to detect and recover from audit processing failures by automatically restarting the audit logging service when it is unexpectedly terminated, ensuring continuous audit logging capability and compliance with CR 2.10. | * The system service definition for auditd was modified to enable automatic restart upon failure. * During testing, the auditd process was manually terminated. * System logs confirmed the detection of the service termination and the successful restart of auditd. * Log entries such as auditd[PID]: Init complete were found after the service restarted, confirming that audit logging was resumed automatically. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 2.10, the security function support to manage the audit processing failure via "Auditd" to enable automatic restart upon failure and the device doesn't have essential function based on the manufactirer's declaration. | Pass |
| Use control | CR 2.11 | Timestamps | Components shall provide the capability to create timestamps (including date and time) for use in audit records. | SL1 | To comply with IEC 62443-4-2 CR 2.11 Timestamp requirements, the Ubuntu 22.04 LTS operating system will be configured to create accurate and synchronized timestamps for use in audit records. The system will ensure the integrity and accuracy of timestamps by using system-wide time synchronization mechanisms and detecting unauthorized | The system’s infrastructure inherently supports the creation and management of detailed audit records through the Event Viewer and journalctl tools . This tool automatically appends precise timestamps to all recorded events, thereby adhering to the IEC 62443-4-2 CR 2.11 specifications. Event Viewer logs contain comprehensive information, including the exact date and time of each event, which is crucial for auditing and troubleshooting purposes. | [20250815 CBTL comment] Documents & Evidence review - Refer to UID01 CR 2.11 RE(1). | Pass |
| Use control | CR 2.11 RE(1) | Time synchronization | Components shall provide the capability to create timestamps that are synchronized with a system wide time source. | SL2 | To comply with IEC 62443-4-2 CR 2.11 RE (1) requirements for time synchronization, the components will be configured to create timestamps synchronized with a system-wide time source. This ensures that all timestamps are accurate and consistent with global standard time, enhancing the integrity and reliability of audit | The implementation of time synchronization in the Debian 12 environment is achieved through the configuration of Chrony (version 4.3), ensuring that all system components generate high-precision, synchronized timestamps. By maintaining an accurate system clock, the logging services (systemd-journald and rsyslog) are capable of including detailed timestamps in all security-related logs, aligned with global standard time. To ensure secure communication and protection against malicious time sources (as described in CR 2.10), the system utilizes Chrony to establish trust with authoritative NTP sources. Chrony is selected as the primary synchronization engine due to its superior security features and efficiency on the RK3568 (AFE-E630) platform, providing robust time correction and hardware clock (RTC) synchronization. Verification of timestamp consistency and accuracy is performed using built-in administrative tools such as journalctl and chronyc. These tools demonstrate that audit records are timestamped with microsecond precision, ensuring the traceability and integrity required by IEC 62443-4-2 CR 2.11 RE (1). |  | Pass |
| Use control | CR 2.11 RE(2) | Protection of time source integrity | The time synchronization mechanism shall provide the capability to detect unauthorized alteration and cause an audit event upon alteration. | SL4 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.12 | Non-repudiation | If a component provides a human user interface, the component shall provide the capability to determine whether a given human user took a particular action. Control elements that are not able to support such capability shall be listed in component documents. | SL1 | To comply with IEC 62443-4-2 CR 2.12 Non-repudiation requirements, The components will be provided and configured to ensure that actions taken by users can be definitively attributed to them. This prevents any user from denying having performed specific actions, such as logging in, changing system configurations, or clearing logs | Debian 12 ensures non-repudiation by utilizing systemd-journald and the auditd framework. The system automatically captures all critical activities, including user logins, privileged command executions, and configuration changes. Each audit record is linked to a unique User ID (UID) and a precise timestamp, ensuring actions are traceable to a specific individual. These logs are stored in protected directories and can be verified via journalctl and ausearch, meeting IEC 62443-4-2 CR 2.12 requirements. |  | Pass |
| Use control | CR 2.12 RE(1) | Non-repudiation for all users | Components shall provide the capability to determine whether a given user (human, software process or device) took a particular action. | SL4 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Use control | CR 2.13 | Use of physical diagnostic and test interfaces | The use of physical diagnostic and test interfaces requirements are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 2.13 | Use of physical diagnostic and test interfaces | Embedded devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging). | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 2.13 | Use of physical diagnostic and test interfaces | Host devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging). | SL2 |  | ID01 chapter | Not evaluation according to manufacturer's request. | N/E |
| Network device requirements | NDR 2.13 | Use of physical diagnostic and test interfaces | Network devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging). | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Embedded device requirements | EDR 2.13 RE(1) | Active monitoring | Embedded devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 2.13 RE(1) | Active monitoring | Host devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Network device requirements | NDR 2.13 RE(1) | Active monitoring | Network devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.01 | Communication integrity | Components shall provide the capability to protect integrity of transmitted information. | SL1 | The content of CR 3.1 RE (1) already includes the requirements of CR 3.1. | The content of CR 3.1 RE (1) already includes the requirements of CR 3.1. |  | Pass |
| System integrity | CR 3.01 RE(1) | Communication authentication | Components shall provide the capability to verify the authenticity of received information during communication. NOTE Both integrity protection and authentication of origin can be achieved without providing confidentiality protection. | SL2 | The comply with IEC 62443 4-2 CR 3.1(1) for Communication integrity or Authentication is to ensure the integrity and authenticity of transmitted information. This step outlines how to use built-in features of Debian 12, specifically OpenSSH, to meet this requirement by protecting the integrity and authenticity of communication. | The Debian 12 platform enforces communication integrity by mandating the use of OpenSSH (Protocol 2) for all remote management activities. Strong Cryptography: The system is restricted to verified cryptographic algorithms, including AES-GCM for data encryption and HMAC-SHA2 for integrity checking, as defined in /etc/ssh/sshd_config. Attack Surface Reduction: All non-secure and unnecessary network services (e.g., L2TP, VPN, and MQTT) are disabled at the service layer, ensuring only the encrypted Port 22 is accessible. Secure Authentication: Direct root access is prohibited, requiring individual user authentication prior to privilege escalation, thus ensuring the authenticity of each session. |  | Pass |
| System integrity | CR 3.02 | Protection from malicious code | The protection from malicious code requirements are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 3.02 | Protection from malicious code | The embedded device shall provide the capability to protect from installation and execution of unauthorized software. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.02 | Protection from malicious code | There shall be mechanisms on host devices that are qualified by the IACS product supplier to provide protection from malicious code. The IACS product supplier shall document any special configuration requirements related to protection from malicious code. | SL1 | The content of HDR 3.2 RE (1) already includes the requirements of HDR 3.02. | The content of HDR 3.2 RE (1) already includes the requirements of HDR 3.02. |  | Pass |
| Network device requirements | NDR 3.02 | Protection from malicious code | The network device shall provide for protection from malicious code. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Software application requirements | SAR 3.02 | Protection from malicious code | The application product supplier shall qualify and document which protection from malicious code mechanisms are compatible with the application and note any special configuration requirements. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.02 RE(1) | Report version of code protection | The host device shall automatically report the software and file versions of protection from malicious code in use (as part of overall logging function). | SL2 | To comply with the requirements of IEC 62443 4-2 HDR 3.2 RE (1) for reporting the version of code protection on Ubuntu 22.04 LTS, the system must automatically report the software and file versions of protection from malicious code in use. This is achieved by utilizing either ClamAV antivirus tool to meet the verification requirements. | The implementation uses built-in capabilities of ClamAV antivirus tool to report the version of the antivirus software and the definition files. These tools are configured to automatically log this information, ensuring compliance with the reporting requirements specified in IEC 62443 4-2 HDR 3.2 RE (1). The logs generated provide clear evidence of the software and file versions in use for protection against malicious code. |  | Pass |
| System integrity | CR 3.03 | Security functionality verification | Components shall provide the capability to support verification of the intended operation of security functions according to IEC 62443-3-3 SR3.03. | SL1 | To comply with IEC 62443-4-2 CR 3.3, the Ubuntu 22.04 LTS operating system must Provide the ability to verify safety functions to ensure the proper functioning of safety controls and provides the ability to verify safety functions during normal operation and ensures the proper functioning of safety controls which support compliance with IEC 62443-4-2 CR 3.3 (1) in accordance with applicable security functionality verification policies and procedures. | Debian 12 provides comprehensive security functionality verification features that are integrated into the AFE-E630 platform to ensure continuous protection. These features support compliance with IEC 62443-4-2 CR 3.3 by allowing users to verify critical security functions during normal operation. The system provides a standardized framework and technical manual for operators to manage and verify the following critical security functions: 1、System Update: Utilizing unattended-upgrades to automatically apply and verify security patches. 2、User Authentication Verification: Testing unauthorized access attempts to ensure pam_faillock and identification policies are correctly enforced. 3、User and Group Permissions Management: Utilizing standard Linux permissions and sudo policies to enforce the principle of least privilege. 4、Firewall and Network Configuration: Verifying network surface reduction via Service Minimization and the ss utility to ensure only Port 22 is accessible. 5、Security Modules Verification: Utilizing EICAR test files to verify ClamAV antivirus effectiveness and checking auditd rule enforcement. 6、System Logs and Auditing: Confirming that audit logs are accurately recorded and synchronized via Chrony and rsyslog in adherence to security policies. 7、Network Security Configuration: Hardening communication channels using OpenSSH (Protocol 2) and verifying cryptographic cipher suites. |  | Pass |
| System integrity | CR 3.03 RE(1) | Security functionality verification during normal operation | Components shall provide the capability to support verification of the intended operation of security functions during normal operations. This RE needs to be carefully implemented to avoid detrimental effects. It may not be suitable for safety systems. | SL4 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.04 | Software and information integrity | Components shall provide the capability to perform or support integrity checks on software, configuration and other information as well as the recording and reporting of the results of these checks or be integrated into a system that can perform or support integrity checks. | SL1 | The system enforces an integrity verification policy using Linux kernel-based mechanisms, including Integrity Measurement Architecture (IMA) and Extended Verification Module (EVM), to cryptographically validate software and configuration files before execution. Unauthorized modifications are detected and blocked, ensuring the integrity of critical system components. | The system enforces an integrity verification policy that uses kernel-level cryptographic mechanisms to validate files before execution. Files that fail these checks are blocked from running, and all validation attempts or unauthorized modifications are logged and routinely reviewed by the security team. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 3.4 RE(1), the security function support to - using SHA-256 for integrity verification through Linux IMA/EVM infrastructure for files, directories, drives, and certificates (file with root permission role only). - The integrity verification policy is defined within the system to enforce checks prior to file execution. - System auditing tools are configured to log all validation attempts and unauthorized modification attempts. | Pass |
| System integrity | CR 3.04 RE(1) | Authenticity of software and information | Components shall provide the capability to perform or support authenticity checks on software, configuration and other information as well as the recording and reporting of the results of these checks or be integrated into a system that can perform or support authenticity checks. | SL2 | Not provided this function to use digital signature verify the authenticity. | Not provided this function to use digital signature verify the authenticity. | Not evaluation according to manufacturer's request. | N/E |
| System integrity | CR 3.04 RE(2) | Automated notification of integrity violations | If the component is performing the integrity check, it shall be capable of automatically providing notification to a configurable entity upon discovery of an attempt to make an unauthorized change. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.05 | Input validation | Components shall validate the syntax, length and content of any input data that is used as an industrial process control input or input via external interfaces that directly impacts the action of the component. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/E |
| System integrity | CR 3.06 | Deterministic output | Components that physically or logically connect to an automation process shall provide the capability to set outputs to a predetermined state if normal operation as defined by the component supplier cannot be maintained. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/E |
| System integrity | CR 3.07 | Error handling | Components shall identify and handle error conditions in a manner that does not provide information that could be exploited by adversaries to attack the IACS. | SL1 | To comply with IEC 62443-4-2 CR 3.7 Error Handling, the Debian 12 operating system will implement an error handling mechanism that ensures error conditions are identified and handled without disclosing information that could be exploited by adversaries to attack the industrial automation control system (IACS). This includes configuring the Ubuntu Error Reporting settings to display error notifications, prevent the disabling of error reporting, and suppress the user interface for critical errors. | Debian 12 includes built-in error handling capabilities that support compliance with IEC 62443-4-2 CR 3.7. By configuring the Ubuntu Error Reporting settings, the system can effectively manage error conditions while maintaining security. Specifically, the settings include displaying error notifications, not disabling error reporting, and preventing the display of the user interface for critical errors. Additionally, login error messages are designed to not disclose information about other users, ensuring that sensitive information is protected. |  | Pass |
| System integrity | CR 3.08 | Session integrity | Components shall provide mechanisms to protect the integrity of communications sessions including: a) the capability to invalidate session identifiers upon user logout or other session termination (including browser sessions); b) the capability to generate a unique session identifier for each session and recognize only session identifiers that are system-generated; and c) the capability to generate unique session identifiers with commonly accepted sources of randomness. | SL2 | To comply with IEC 62443-4-2 CR 3.8 Session Integrity, the Ubuntu 22.04 LTS operating system will implement mechanisms to protect the integrity of communication sessions. This includes invalidating session identifiers upon user logout, generating unique session identifiers, and using accepted sources of randomness to ensure session security. | Ubuntu 22.04 LTS incorporates several features that align with the IEC 62443-4-2 CR 3.8 requirements for session integrity. These features include the management of SSH sessions, where each session is securely handled to maintain communication integrity. 1.Unique Session Identifiers: SSH sessions on Ubuntu generate unique session identifiers for each connection. These identifiers are managed securely, ensuring that they cannot be reused or tampered with. 2.Session Termination: Upon user logout or session termination, the SSH session is immediately invalidated, ensuring that no lingering identifiers can be exploited. 3.Secure Randomness for Session Identifiers: The SSH service on Ubuntu uses a Cryptographically Secure Pseudo-Random Number Generator (CSPRNG) to generate session identifiers and cryptographic keys. This ensures that all session identifiers are robust against prediction and tampering. |  | Pass |
| System integrity | CR 3.09 | Protection of audit information | Components shall protect audit information, audit logs, and audit tools (if present) from unauthorized access, modification and deletion. | SL2 | To comply with IEC 62443-4-2 CR 3.9, the Ubuntu 22.04 LTS operating system must implement mechanisms to protect audit information, audit logs, and audit tools from unauthorized access, modification, and deletion. This ensures the integrity and availability of audit data, which is crucial for security breach recovery, investigations, and related efforts. | Ubuntu 22.04 LTS utilizes the event logging system to capture and protect audit information. The system includes features such as secure storage, access controls, and integrity checks. Ubuntu's default logging system, rsyslog, and auditd are configured to ensure that audit logs are protected from unauthorized access and modification, thus meeting the requirements of IEC 62443-4-2 CR 3.9. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 3.9, the security function support to protect audit information, audit logs, and audit tools via Ubuntu's default logging system, rsyslog, and auditd from unauthorized access and modification | Pass |
| System integrity | CR 3.09 RE(1) | Audit records on write-once media | Components shall provide the capability to store audit records on hardware-enforced write-once media. | SL4 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.10 | Support for updates | The support for updates requirements are component-specific and can be located as requirements for each specific device type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 3.10 | Support for updates | The embedded device shall support the ability to be updated and upgraded. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.10 | Support for updates | Host devices shall support the ability to be updated and upgraded. | SL1 | The content of HDR 3.10 RE(1) already includes the requirements of HDR 3.10. | The content of HDR 3.10 RE(1) already includes the requirements of HDR 3.10. |  | Pass |
| Network device requirements | NDR 3.10 | Support for updates | Network devices shall support the ability to be updated and upgraded. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Embedded device requirements | EDR 3.10 RE(1) | Update authenticity and integrity | The embedded device shall validate the authenticity and integrity of any software update or upgrade prior to installation. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.10 RE(1) | Update authenticity and integrity | Host devices shall validate the authenticity and integrity of any software update or upgrade prior to installation. | SL2 | To comply with IEC 62443-4-2 CR 3.10 and HDR 3.10 RE(1) on Support for Updates and Update Authenticity and Integrity, the Debian 12 operating system must support secure software updates and upgrades. It shall ensure that the authenticity and integrity of any update are cryptographically validated prior to installation. | Debian 12 includes built-in update mechanisms through its Advanced Packaging Tool (APT) and Update Manager, which provide robust support for controlled software updates and upgrades. These tools validate the authenticity of updates using GPG (GNU Privacy Guard) digital signatures, and the integrity of the packages using SHA-256 hashing. GPG keys used by Canonical are based on the RSA 4096-bit algorithm, meeting the security strength required by IEC 62443-4-2. Updates are only applied if both the signature and hash verification succeed, ensuring secure and trusted installation. |  | Pass |
| Network device requirements | NDR 3.10 RE(1) | Update authenticity and integrity | Network devices shall validate the authenticity and integrity of any software update or upgrade prior to installation. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.11 | Physical tamper resistance and detection | The physical tamper resistance and detection requirements are component-specific and can be located as requirements for each specific device type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 3.11 | Physical tamper resistance and detection | The embedded device shall provide tamper resistance and detection mechanisms to protect against unauthorized physical access into the device. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.11 | Physical tamper resistance and detection | Host devices shall provide the capability to support tamper resistance and detection mechanisms to protect against unauthorized physical access into the device. | SL2 | N/E | N/E | [20250815 CBTL comment] Not evaluation according to manufacturer's request. | N/E |
| Network device requirements | NDR 3.11 | Physical tamper resistance and detection | Network devices shall provide tamper resistance and detection mechanisms to protect against unauthorized physical access into the device. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Embedded device requirements | EDR 3.11 RE(1) | Notification of a tampering attempt | The embedded device shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.11 RE(1) | Notification of a tampering attempt | Host devices shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Network device requirements | NDR 3.11 RE(1) | Notification of a tampering attempt | Network devices shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.12 | Provisioning product supplier roots of trust | The provisioning product supplier roots of trust requirements are component-specific and can be located as requirements for each specific device type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 3.12 | Provisioning product supplier roots of trust | Embedded devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.12 | Provisioning product supplier roots of trust | Host devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device. | SL2 | Debian 12 on ARM uses SoC hardware security features like TrustZone and TEE with secure boot to protect the product supplier’s root of trust. Certificates and keys are securely managed within the trusted environment to prevent unauthorized access. The boot process verifies each stage cryptographically, ensuring software integrity and system security. | Secure Boot on ARM starts from immutable BootROM verifying all boot stages cryptographically. Keys and certificates are provisioned and managed only inside the TEE, isolated from the normal OS. Security events and key operations are logged securely for audit and compliance. |  | Pass |
| Network device requirements | NDR 3.12 | Provisioning product supplier roots of trust | Network devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.13 | Provisioning asset owner roots of trust | The provisioning asset owner roots of trust requirements are component-specific and can be located as requirements for each specific device type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 3.13 | Provisioning asset owner roots of trust | Embedded devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security zone. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.13 | Provisioning asset owner roots of trust | Host devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security zone. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/E |
| Network device requirements | NDR 3.13 | Provisioning asset owner roots of trust | Network devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security zone. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| System integrity | CR 3.14 | Integrity of the boot process | The integrity of the boot process requirements are component-specific and can be located as requirements for each specific device type in Clauses 12 through 15. | N/A |  |  | Not a requirement | N/A |
| Embedded device requirements | EDR 3.14 | Integrity of the boot process | Embedded devices shall verify the integrity of the firmware, software, and configuration data needed for the component’s boot and runtime processes prior to use. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.14 | Integrity of the boot process | Host devices shall verify the integrity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | SL1 | The content of HDR 3.14 RE(1) already includes the requirements of HDR 3.14. | The content of HDR 3.14 RE(1) already includes the requirements of HDR 3.14. | [20250815 CBTL comment] Documents & Evidence review - refer to CR 3.14 RE(1) | Pass |
| Network device requirements | NDR 3.14 | Integrity of the boot process | Network devices shall verify the integrity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Embedded device requirements | EDR 3.14 RE(1) | Authenticity of the boot process | Embedded devices shall use the component’s product supplier roots of trust to verify the authenticity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Host device requirements | HDR 3.14 RE(1) | Authenticity of the boot process | Host devices shall use the component’s product supplier roots of trust to verify the authenticity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | SL2 | The boot process enforces cryptographic verification of all components involved in OS initialization, including firmware, bootloader, kernel, and critical modules. Hardware-based trusted execution environments combined with Secure Boot establish a hardware root of trust and enforce a verified boot chain, ensuring integrity and authenticity in compliance with IEC 62443 4-2 HDR 3.14. | Trusted execution environments securely store cryptographic keys used for signature validation of boot components. The secure bootloader validates digital signatures before transferring control to the OS kernel. Secure Boot enforces signature and integrity checks at each stage of the boot sequence, aborting on verification failure. Comprehensive audit logs record all verification events to support security monitoring and forensic analysis. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 3.14 RE(1), the security function support to Secure Boot and hardware-based trusted execution environments functionalities to ensure the integrity and authenticity of the boot process. - The boot process follows a chain of trust: ROM Code → Preloader → U-Boot → Linux Kernel (refer to flow chart of https://mediatek.gitlab.io/aiot/doc/aiot-dev-guide/master/_images/sw_yocto_secure-boot_workflow.png) - The secure bootloader verifies the digital signatures of firmware and kernel images - Any failure in signature validation or integrity checks halts the boot sequence - SHA256 is used for integrity verification throughout the boot chain - RSA3072 for authenticity check by default based on the mediatek technical docunment (https://mediatek.gitlab.io/aiot/doc/aiot-dev-guide/master/sw/yocto/secure-boot.html) | Pass |
| Network device requirements | NDR 3.14 RE(1) | Authenticity of the boot process | Network devices shall use the component’s product supplier roots of trust to verity the authenticity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process. | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Data confidentiality | CR 4.01 | Information confidentiality | Components shall a) provide the capability to protect the confidentiality of information at rest for which explicit read authorization is supported; and b) support the protection of the confidentiality of information in transit as defined in IEC 62443-3-3 SR 4.1. | SL1 | LUKS encryption is used to protect data at rest; TLS 1.2/1.3 is enforced to secure data in transit on Debian 12, complying with IEC 62443-4-2 CR 4.1. | Encrypted partition uses LUKS (AES-256) and is only mounted after manual unlock. TLS 1.0/1.1 is disabled via global OpenSSL configuration (/etc/ssl/openssl.cnf), which mandates AES-GCM based ciphersuites and ensures the integrity and confidentiality of data in transit. |  | Pass |
| Data confidentiality | CR 4.02 | Information persistence | Components shall provide the capability to erase all information, for which explicit read authorization is supported, from components to be released from active service and/or decommissioned. | SL2 | System ensures secure erasure of all authorized readable data—including files, configurations, credentials, and memory content—prior to decommissioning, using built-in Ubuntu 22.04 LTS functions. | Secure-delete tools (srm/sfill) used to erase files, directories, and free disk space; memtester/sysctl used for volatile memory; no swap configured (swapon --summary = empty); logs, certificates, and user history are cleared. Full user directory deleted upon system decommissioning. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 4.2, the security mechanism below support to securely erased information. - Securely delete files and directories - Wipe free disk space - Clear volatile memory (RAM/shared memory) - Remove application-specific and residual sensitive data (e.g., logs, certificates) - Avoid swap usage entirely (in this system) to prevent data persistence | Pass |
| Data confidentiality | CR 4.02 RE(1) | Erase of shared memory resources | Components shall provide the capability to protect against unauthorized and unintended information transfer via volatile shared memory resources. Volatile memory resources are those that generally do not retain information after being released to memory management. However, there are attacks against random access memory (RAM) which might extract key material or other confidential data before it is actually over-written. Therefore, when volatile shared memory is released back to the control system for use by a different user, all unique data and connections to unique data need to be purged from the resource so it is not visible or accessible to the new user. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Data confidentiality | CR 4.02 RE(2) | Erase verification | Components shall provide the capability to verify that the erasure of information occurred. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Data confidentiality | CR 4.03 | Use of cryptography | If cryptography is required, the component shall use cryptographic security mechanisms according to internationally recognized and proven security practices and recommendations. | SL1 | The system uses OpenSSL 3.x for cryptographic functions, supporting TLS 1.3 encryption, strong SSH algorithms, APT package integrity via GPG, and NTS for time synchronization. Data protection is ensured with AES encryption, eCryptfs, and GNOME Keyring. Cipher suites comply with SOGIS Agreed Cryptographic Mechanisms v1.3 and BSI-TR-02102-4, with IANA as a secondary reference. | * OpenSSL Version and TLS 1.3 Cipher Suites * SSH Configuration * APT Package Integrity * Network Time Security Configuration * eCryptfs and GNOME Keyring | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 4.3, the cipher suite and cryptographic security mechanisms was complied with the best pratice recommendations. - the system uses eCryptfs and fscrypt for file-level encryption with AES-256. - GNOME Keyring is used to encrypt sensitive data such as passwords and keys with AES-256 AES-128. - TLS Cipher Suites follow SOGIS Agreed Cryptographic Mechanisms v1.3 standards - SSH Cipher Suites follow BSI-TR-02102-4 and IANA (openSSHv2) - Ubuntu Digital signatures using RSA 4096-bit GPG keys for update authenticity and SHA256 for update integrity based on HDR3.10(1). - Advantech Platform key RSA2048 - RSA2048 for authenticity check by default and SHA256 is used for integrity verification throughout the boot chain based on HDR3.14(1). | Pass |
| Restricted data flow | CR 5.01 | Network segmentation | Components shall support a segmented network to support zones and conduits, as needed, to support the broader network architecture based on logical segmentation and criticality. | SL1 | Logical network segmentation is implemented using two Ethernet interfaces, each configured with both static and dynamic IP addresses. A host-based firewall applies a default-deny policy, permitting only SSH from a trusted subnet and outbound DNS, HTTP, HTTPS, and NTP. Non-essential services are disabled to minimize exposure, in alignment with IEC 62443-4-2 CR 5.1. | Network configuration confirms segmentation between internal and external domains using interface-level IP assignment. Firewall rules enforce a deny-by-default policy, allowing only approved services. Non-essential services such as multicast discovery and printing are disabled. The system exposes only authorized ports, with no unintended services active. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 5.1, the security function support to network segmentation via netplan, and ufw (host-based firewall). | Pass |
| Restricted data flow | CR 5.02 | Zone boundary protection | The zone boundary protection requirements are network-component-specific and can be located as requirements for network devices in Clause 15. | N/A |  |  | Not a requirement | N/A |
| Network device requirements | NDR 5.02 | Zone boundary protection | A network device at a zone boundary shall provide the capability to monitor and control communications at zone boundaries to enforce the compartmentalization defined in the risk-based zones and conduits model. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Network device requirements | NDR 5.02 RE(1) | Deny all, permit by exception | The network component shall provide the capability to deny network traffic by default and allow network traffic by exception (also termed deny all, permit by exception). | SL2 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Network device requirements | NDR 5.02 RE(2) | Island mode | The network component shall provide the capability to protect against any communication through the control system boundary (also termed island mode). NOTE 1 Examples of when this capability can be used include where a security violation and/or breach has been detected within the control system, or an attack is occurring at the enterprise level. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Network device requirements | NDR 5.02 RE(3) | Fail close | The network component shall provide the capability to protect against any communication through the control system boundary when there is an operational failure of the boundary protection mechanisms (also termed fail close). NOTE 2 Examples of when this capability can be used include scenarios where a hardware failure or power failure causes boundary protection devices to function in a degraded mode or fail entirely. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Restricted data flow | CR 5.03 | General-purpose person-to-person communication restrictions | The general-purpose person-to-person communication restriction requirements are network-component-specific and can be located as requirements for network devices in Clause 15. | N/A |  |  | Not a requirement | N/A |
| Network device requirements | NDR 5.03 | General purpose, person-to-person communication restrictions | A network device at a zone boundary shall provide the capability to protect against general purpose, person-to-person messages from being received from users or systems external to the control system. | SL1 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Restricted data flow | CR 5.04 | Application partitioning | There is no component level requirement associated with IEC 62443-3-3 SR 5.04. | N/A |  |  | Not a requirement | N/A |
| Timely response to events | CR 6.01 | Audit log accessibility | Components shall provide the capability for authorized humans and/or tools to access audit logs on a read-only basis. | SL1 | To compliance with IEC 62443-4-2 CR 6.1 Audit log accessibility requirements by using the built-in event viewer capabilities of the Ubuntu 22.04 LTS operating system. This method ensures that authorized personnel and tools can access audit logs on a read-only basis | ​Ubuntu 22.04 LTS includes robust logging and audit capabilities through its system logs and journalctl tool. These tools provide read-only access to audit logs for authorized users, meeting the requirements of IEC 62443-4-2 CR 6.1. The configuration ensures that logs are protected from unauthorized modification while remaining accessible for review and analysis. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 6.1, the security function support authorized user (root and Group adm) to read-only Audit log accessibility requirements by using the built-in event viewer via its system logs and journalctl tool. | Pass |
| Timely response to events | CR 6.01 RE(1) | Programmatic access to audit logs | Components shall provide programmatic access to audit records by either using an application programming interface (API) or sending the audit records to a centralized system. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Timely response to events | CR 6.02 | Continuous monitoring | Components shall provide the capability to be continuously monitored using commonly accepted security industry practices and recommendations to detect, characterize and report security breaches in a timely manner. | SL2 | To meet the requirements of IEC 62443-4-2 CR 6.2: Continuous Monitoring for the Ubuntu 22.04 LTS operating system. The goal is to provide continuous monitoring using commonly accepted security industry practices and recommendations to detect, characterize, and report security breaches promptly. | ​Ubuntu 22.04 LTS provides built-in tools and features that can be leveraged to meet the requirements of IEC 62443-4-2 CR 6.2. These include: ​Auditd: A user-space component for monitoring and logging system events and activities. ​Fail2ban: An intrusion prevention software framework that can be used to detect and prevent security breaches. ​Logwatch: A log analyzer that can be used to monitor and report on various system logs, including security-related events. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 6.2, the security function support to continuous monitoring to detect, characterize, and report security breaches promptly via Auditd, Fail2ban, Logwatch. | Pass |
| Resource availability | CR 7.01 | Denial of service protection | Components shall provide the capability to maintain essential functions when operating in a degraded mode as the result of a DoS event. | SL1 | The system implements Denial of Service (DoS) protection using Ubuntu 22.04 LTS built-in tools including ufw, fail2ban, and sysctl. These mechanisms help limit incoming connection rates, block unauthorized access attempts, and prevent system overload due to brute-force or network-layer attacks. | * ufw blocks all unused ports and limits SSH rate. * fail2ban bans IPs after failed SSH logins. * ICMP and SYN flood mitigated via sysctl. * All logs reviewable via journalctl | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.1 RE(1), the security function support to protect against login failure attacks, ping attacks, and TCP/UDP attacks via security mechanisms include ufw limit for brute-force attempts, fail2ban (1800s) for login failure attacks, sysctl settings for ping flood attacks and SYN flood attacks, iptables rules to manage TCP/UDP flood attacks. | Pass |
| Resource availability | CR 7.01 RE(1) | Manage communication load from component | Components shall provide the capability to mitigate the effects of information and/or message flooding types of DoS events. | SL2 | The system implements controls to manage internal communication load by limiting service-level resource usage, prioritizing essential functions, and applying per-connection limitations. This ensures that no single component overloads the system during normal or high-load operations. | * CPU and memory limits are configured via systemd for each system service. * Background and non-essential services are assigned lower priority. * SSH and other services are rate-limited per IP using ufw. * iptables restricts the number of concurrent sessions from a single IP. * ssential services are identified and protected to ensure uninterrupted operation under load. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.1 RE(1), the security function support to ensures that no single component overloads the system during normal or high-load operations including systemd for each system service CPU and memory limits, ufw limit for brute-force attempts, iptables rules to manage TCP/UDP flood attacks. | Pass |
| Resource availability | CR 7.02 | Resource Management | Components shall provide the capability to limit the use of resources by security functions to protect against resource exhaustion. | SL1 | Ubuntu 22.04 LTS with cgroup v2 is configured to limit CPU, memory, and I/O usage of system services using systemd resource control to ensure essential functions remain available under high load. | Resource limits were applied using systemd directives (CPUQuota, MemoryMax) in a custom cpu-hog.service and verified via journal logs, cgroup files, and real-time tools like systemd-cgtop. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.2, the security function support to use the tools ensure that lower-priority processes do not interfere with higher-priority control system operations via systemd for managing system services, cgroup v2 (control groups) for limiting resource usage(CPU, memory, and I/O resources). | Pass |
| Resource availability | CR 7.03 | Control System backup | Components shall provide the capability to participate in system level backup operations in order to safeguard the component state (user- and system-level information). The backup process shall not affect the normal component operations. | SL1 | ​The content of CR 7.3 RE(1) already includes the requirements of CR 7.3. | ​The content of CR 7.3 RE(1) already includes the requirements of CR 7.3. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.3, the security function support to Control System backup and Backup Integrity Verification via the Timeshift tool. | Pass |
| Resource availability | CR 7.03 RE(1) | Backup integrity verification | Components shall provide the capability to validate the integrity of backed up information prior to the initiation of a restore of that information. | SL2 | To comply with IEC 62443 4-2 CR 7.3 and CR 7.3 RE(1) requirements for Control System backup and Backup Integrity Verification on the Ubuntu 22.04 LTS operating system, utilizing the Timeshift tool. The backup process is designed to ensure system-level backups without affecting normal component operations and includes integrity verification mechanisms. | The Timeshift tool on Ubuntu 22.04 LTS provides comprehensive backup capabilities essential for recovering from control system failures or misconfigurations. By automating backups, Timeshift ensures all necessary files are captured, thus minimizing operator workload and maximizing system reliability. Additionally, the tool supports backup integrity verification, ensuring that the data integrity is validated before any restore operation, complying with CR 7.3 RE(1). | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.3 RE(1), the security function support that Timeshift automatically verifies the bakup including the integrity of the snapshot. | Pass |
| Resource availability | CR 7.04 | Control system recovery and reconstitution | Components shall provide the capability to be recovered and reconstituted to a known secure state after a disruption or failure. | SL1 | To comply with IEC 62443 4-2 CR 7.4 Control System Recovery and Reconstitution, Ubuntu 22.04 LTS provides built-in capabilities to ensure that the system can be recovered and reconstituted to a known secure state after a disruption or failure. This compliance includes setting all system parameters to secure values, reinstalling security-critical patches, reestablishing security-related configuration settings, ensuring system documentation and operating procedures are available, and restoring information from recent secure backups. | Ubuntu 22.04 LTS includes several built-in tools and features that facilitate system recovery and reconstitution. These tools, such as Timeshift for system backups, APT for package management, and UFW for firewall configuration, allow the system to be restored to a secure state. Detailed documentation and support from the Ubuntu community and Canonical ensure that the procedures align with IEC 62443 4-2 requirements. These features collectively provide the necessary infrastructure to meet the control system recovery and reconstitution criteria | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.4, the security function support to recovery and reconstitution the secure status via Timeshift for system backups, APT for package management, and UFW for firewall configuration, allow the system to be restored to a secure state. | Pass |
| Resource availability | CR 7.05 | Emergency Power | There is no component level requirement associated with IEC 62443-3-3 SR 7.05. | N/A |  |  | Not a requirement | N/A |
| Resource availability | CR 7.06 | Network and security configuration settings | Components shall provide the capability to be configured according to recommended network and security configurations as described in guidelines provided by the control system supplier. The component shall provide an interface to the currently deployed network and security configuration settings. | SL1 | To meet the requirements of IEC 62443-4-2 CR 7.6: Network and Security Configuration Settings for the Ubuntu 22.04 LTS operating system. The goal is to provide the capability to configure the system according to recommended network and security configurations and to report on the currently deployed settings. | To align with the specified security guidelines, Ubuntu 22.04 LTS has been configured to leverage its built-in security features, including UFW (Uncomplicated Firewall) and specific network configuration adjustments. The configuration process is thoroughly documented, capturing the activation of the firewall, adjustments to network settings, and the disabling of unnecessary services and protocols. Regular audits are performed to maintain a high standard of security compliance, with all changes and reviews being properly recorded. The Arm platform provides network security feature settings which can be referenced in: UID03 - [Ubuntu][RSB-3810] Security Guidelines.docx | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.6 and UID03, the security function support to configure the system according to recommended network and security configurations and to report on the currently deployed settings. | Pass |
| Resource availability | CR 7.06 RE(1) | Machine-readable reporting of current security settings | Components shall provide the capability to generate a report listing the currently deployed security settings in a machine-readable format. | SL3 |  |  | Not evaluation according to manufacturer's request. | N/A |
| Resource availability | CR 7.07 | Least functionality | Components shall provide the capability to specifically restrict the use of unnecessary functions, ports, protocols and/or services. | SL1 | Ubuntu 22.04 LTS is configured to disable unused services and block unnecessary ports, ensuring only essential IACS functions are enabled. | Disabled services via systemctl disable; restricted ports using ufw default deny and ufw allow; verified configuration with ss and ufw status. | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.7 and UID03 Security Guidelines, the security function support to (i) Disable Unnecessary Services (ii) Configure the Uncomplicated Firewall (UFW) | Pass |
| Resource availability | CR 7.08 | Control system component inventory | Components shall provide the capability to support a control system component inventory according to IEC 62443-3-3 SR 7.08. | SL2 | To meet the IEC 62443-4-2 CR 7.8 requirements for control system component inventory using Ubuntu 22.04 LTS. The objective is to utilize the Ubuntu Landscape tool to manage and maintain a comprehensive inventory of control system components, including server management, update management, storage management, and network management. | The implementation adheres to the guidelines provided in IEC 62443-4-2 CR 7.8 by leveraging the functionalities of Ubuntu Landscape. This tool supports server management, user management, update management, storage management, and network management, ensuring compatibility with IEC 62443-2-4 and providing a mechanism to augment the overall component inventory | [20250815 CBTL comment] Documents & Evidence review - After reviewed the UID01 CR 7.8, the security function support to manage and maintain a comprehensive inventory of control system components via the Ubuntu Landscape tool. | Pass |

End of Attachment 1

| IEC 62443-4-2 ID | Requirement Name | Results-Remarks | Verdict |
| --- | --- | --- | --- |
| CCSC 1 | Support of essential functions | Not in scope | N/A |
| CCSC 2 | Compensating countermeasures | Not in scope | N/A |
| CCSC 3 | Least privilege | Not in scope | N/A |
| CCSC 4 | Software development process | Not in scope | N/A |
| CR 1.01 | Human user identification and authentication |  | Pass |
| CR 1.01 RE(1) | Unique identification and authentication |  | Pass |
| CR 1.01 RE(2) | Multifactor authentication for all interfaces | Not in scope | N/A |
| CR 1.02 | Software process and device identification and authentication | Not evaluated on customer request | N/E |
| CR 1.02 RE(1) | Unique identification and authentication | Not in scope | N/A |
| CR 1.03 | Account management |  | Pass |
| CR 1.04 | Identifier management |  | Pass |
| CR 1.05 | Authenticator management |  | Pass |
| CR 1.05 RE(1) | Hardware security for authenticators | Not in scope | N/A |
| CR 1.06 | Wireless access management | Not in scope | N/A |
| NDR 1.06 | Wireless access management | Not in scope | N/A |
| NDR 1.06 RE(1) | Unique identification and authentication | Not in scope | N/A |
| CR 1.07 | Strength of password-based authentication |  | Pass |
| CR 1.07 RE(1) | Password generation and lifetime restrictions for human users | Not in scope | N/A |
| CR 1.07 RE(2) | Password lifetime restrictions for all users (human, software process, or device) | Not in scope | N/A |
| CR 1.08 | Public key infrastructure certificates | Not evaluated on customer request | N/E |
| CR 1.09 | Strength of public key-based authentication | Not evaluated on customer request | N/E |
| CR 1.09 RE(1) | Hardware security for public key-based authentication | Not in scope | N/A |
| CR 1.10 | Authenticator feedback |  | Pass |
| CR 1.11 | Unsuccessful login attempts |  | Pass |
| CR 1.12 | System use notification |  | Pass |
| CR 1.13 | Access via untrusted networks | Not in scope | N/A |
| NDR 1.13 | Access via untrusted networks | Not in scope | N/A |
| NDR 1.13 RE(1) | Explicit access request approval | Not in scope | N/A |
| CR 1.14 | Strength of symmetric key-based authentication | Not evaluated on customer request | N/E |
| CR 1.14 RE(1) | Hardware security for symmetric key-based authentication | Not in scope | N/A |
| CR 2.01 | Authorization enforcement |  | Pass |
| CR 2.01 RE(1) | Authorization enforcement for all users (humans, software processes and devices) |  | Pass |
| CR 2.01 RE(2) | Permission mapping to roles |  | Pass |
| CR 2.01 RE(3) | Supervisor override | Not in scope | N/A |
| CR 2.01 RE(4) | Dual approval | Not in scope | N/A |
| CR 2.02 | Wireless use control | Not in scope | N/A |
| CR 2.03 | Use control for portable and mobile devices | Not in scope | N/A |
| CR 2.04 | Mobile code | Not in scope | N/A |
| EDR 2.04 | Mobile code | Not in scope | N/A |
| HDR 2.04 | Mobile code |  | Pass |
| NDR 2.04 | Mobile code | Not in scope | N/A |
| SAR 2.04 | Mobile code | Not in scope | N/A |
| EDR 2.04 RE(1) | Mobile code authenticity check | Not in scope | N/A |
| HDR 2.04 RE(1) | Mobile code authenticity check | Not evaluated on customer request | N/E |
| NDR 2.04 RE(1) | Mobile code authenticity check | Not in scope | N/A |
| SAR 2.04 RE(1) | Mobile code authenticity check | Not in scope | N/A |
| CR 2.05 | Session lock |  | Pass |
| CR 2.06 | Remote session termination |  | Pass |
| CR 2.07 | Concurrent session control | Not in scope | N/A |
| CR 2.08 | Auditable events |  | Pass |
| CR 2.09 | Audit storage capacity |  | Pass |
| CR 2.09 RE(1) | Warn when audit record storage capacity threshold reached | Not in scope | N/A |
| CR 2.10 | Response to audit processing failures |  | Pass |
| CR 2.11 | Timestamps |  | Pass |
| CR 2.11 RE(1) | Time synchronization |  | Pass |
| CR 2.11 RE(2) | Protection of time source integrity | Not in scope | N/A |
| CR 2.12 | Non-repudiation |  | Pass |
| CR 2.12 RE(1) | Non-repudiation for all users | Not in scope | N/A |
| CR 2.13 | Use of physical diagnostic and test interfaces | Not in scope | N/A |
| EDR 2.13 | Use of physical diagnostic and test interfaces | Not in scope | N/A |
| HDR 2.13 | Use of physical diagnostic and test interfaces | Not evaluated on customer request | N/E |
| NDR 2.13 | Use of physical diagnostic and test interfaces | Not in scope | N/A |
| EDR 2.13 RE(1) | Active monitoring | Not in scope | N/A |
| HDR 2.13 RE(1) | Active monitoring | Not in scope | N/A |
| NDR 2.13 RE(1) | Active monitoring | Not in scope | N/A |
| CR 3.01 | Communication integrity |  | Pass |
| CR 3.01 RE(1) | Communication authentication |  | Pass |
| CR 3.02 | Protection from malicious code | Not in scope | N/A |
| EDR 3.02 | Protection from malicious code | Not in scope | N/A |
| HDR 3.02 | Protection from malicious code |  | Pass |
| NDR 3.02 | Protection from malicious code | Not in scope | N/A |
| SAR 3.02 | Protection from malicious code | Not in scope | N/A |
| HDR 3.02 RE(1) | Report version of code protection |  | Pass |
| CR 3.03 | Security functionality verification |  | Pass |
| CR 3.03 RE(1) | Security functionality verification during normal operation | Not in scope | N/A |
| CR 3.04 | Software and information integrity |  | Pass |
| CR 3.04 RE(1) | Authenticity of software and information | Not evaluated on customer request | N/E |
| CR 3.04 RE(2) | Automated notification of integrity violations | Not in scope | N/A |
| CR 3.05 | Input validation | Not evaluated on customer request | N/E |
| CR 3.06 | Deterministic output | Not evaluated on customer request | N/E |
| CR 3.07 | Error handling |  | Pass |
| CR 3.08 | Session integrity |  | Pass |
| CR 3.09 | Protection of audit information |  | Pass |
| CR 3.09 RE(1) | Audit records on write-once media | Not in scope | N/A |
| CR 3.10 | Support for updates | Not in scope | N/A |
| EDR 3.10 | Support for updates | Not in scope | N/A |
| HDR 3.10 | Support for updates |  | Pass |
| NDR 3.10 | Support for updates | Not in scope | N/A |
| EDR 3.10 RE(1) | Update authenticity and integrity | Not in scope | N/A |
| HDR 3.10 RE(1) | Update authenticity and integrity |  | Pass |
| NDR 3.10 RE(1) | Update authenticity and integrity | Not in scope | N/A |
| CR 3.11 | Physical tamper resistance and detection | Not in scope | N/A |
| EDR 3.11 | Physical tamper resistance and detection | Not in scope | N/A |
| HDR 3.11 | Physical tamper resistance and detection | Not evaluated on customer request | N/E |
| NDR 3.11 | Physical tamper resistance and detection | Not in scope | N/A |
| EDR 3.11 RE(1) | Notification of a tampering attempt | Not in scope | N/A |
| HDR 3.11 RE(1) | Notification of a tampering attempt | Not in scope | N/A |
| NDR 3.11 RE(1) | Notification of a tampering attempt | Not in scope | N/A |
| CR 3.12 | Provisioning product supplier roots of trust | Not in scope | N/A |
| EDR 3.12 | Provisioning product supplier roots of trust | Not in scope | N/A |
| HDR 3.12 | Provisioning product supplier roots of trust |  | Pass |
| NDR 3.12 | Provisioning product supplier roots of trust | Not in scope | N/A |
| CR 3.13 | Provisioning asset owner roots of trust | Not in scope | N/A |
| EDR 3.13 | Provisioning asset owner roots of trust | Not in scope | N/A |
| HDR 3.13 | Provisioning asset owner roots of trust | Not evaluated on customer request | N/E |
| NDR 3.13 | Provisioning asset owner roots of trust | Not in scope | N/A |
| CR 3.14 | Integrity of the boot process | Not in scope | N/A |
| EDR 3.14 | Integrity of the boot process | Not in scope | N/A |
| HDR 3.14 | Integrity of the boot process |  | Pass |
| NDR 3.14 | Integrity of the boot process | Not in scope | N/A |
| EDR 3.14 RE(1) | Authenticity of the boot process | Not in scope | N/A |
| HDR 3.14 RE(1) | Authenticity of the boot process |  | Pass |
| NDR 3.14 RE(1) | Authenticity of the boot process | Not in scope | N/A |
| CR 4.01 | Information confidentiality |  | Pass |
| CR 4.02 | Information persistence |  | Pass |
| CR 4.02 RE(1) | Erase of shared memory resources | Not in scope | N/A |
| CR 4.02 RE(2) | Erase verification | Not in scope | N/A |
| CR 4.03 | Use of cryptography |  | Pass |
| CR 5.01 | Network segmentation |  | Pass |
| CR 5.02 | Zone boundary protection | Not in scope | N/A |
| NDR 5.02 | Zone boundary protection | Not in scope | N/A |
| NDR 5.02 RE(1) | Deny all, permit by exception | Not in scope | N/A |
| NDR 5.02 RE(2) | Island mode | Not in scope | N/A |
| NDR 5.02 RE(3) | Fail close | Not in scope | N/A |
| CR 5.03 | General-purpose person-to-person communication restrictions | Not in scope | N/A |
| NDR 5.03 | General purpose, person-to-person communication restrictions | Not in scope | N/A |
| CR 5.04 | Application partitioning | Not in scope | N/A |
| CR 6.01 | Audit log accessibility |  | Pass |
| CR 6.01 RE(1) | Programmatic access to audit logs | Not in scope | N/A |
| CR 6.02 | Continuous monitoring |  | Pass |
| CR 7.01 | Denial of service protection |  | Pass |
| CR 7.01 RE(1) | Manage communication load from component |  | Pass |
| CR 7.02 | Resource Management |  | Pass |
| CR 7.03 | Control System backup |  | Pass |
| CR 7.03 RE(1) | Backup integrity verification |  | Pass |
| CR 7.04 | Control system recovery and reconstitution |  | Pass |
| CR 7.05 | Emergency Power | Not in scope | N/A |
| CR 7.06 | Network and security configuration settings |  | Pass |
| CR 7.06 RE(1) | Machine-readable reporting of current security settings | Not in scope | N/A |
| CR 7.07 | Least functionality |  | Pass |
| CR 7.08 | Control system component inventory |  | Pass |

End of Attachment 2

| ID | Name of the Document | Version |
| --- | --- | --- |
| UID01 | UID01 - [Ubuntu][RSB-3810] Statement and Evidence | V1 |
| UID02 | UID02 - [Ubuntu][RSB-3810] Comprehensive Use of Cryptography in Ubuntu 22.04 | V1 |
| UID03 | UID03 - [Ubuntu][RSB-3810] Security Guidelines | V1 |

End of Attachment 3